## jensa_by_component
ITEM | ACTION | DUE DATE | ADDL DUE DATE | FURTHER DOCUMENTATION
JENSA compressor
| Check lubricant oil level, top up as required | daily |  | Compressor Instruction Manual 2nd Edition – Rev 4 FINAL page 30-42
| Check base frame lubricant pressure | daily
| Check cooling system flow, temperature, pressure | daily
| Check operation of control systems | daily | every 4000 hours
| Check inlet filter pressure drop | daily
| Verify inlet, interstage, and outlet pressures are normal | daily
| Check for abnormal noise or vibration | daily
| Check leak detection system gauges on both heads | daily | every 4000 hours
| Disassemble and check inlet filter, replace/clean as required | every 300 hours
| Change oil and oil filter elements, clean or replace strainer element | after first 50 hours | every 1500 hours | Ibid. page 32-33
| Diaphragm and o-ring seal inspection/replacement | every 4000 hours |  | Ibid. page 34-36
| Inspect check valves, clean or replace as required | every 3000 hours |  | Ibid. page 37. Operational note: these check valves wear out faster with use of gases heavier than helium
| Inspect oil inlet check valves, clean or replace as required | every 3000 hours |  | Ibid. page 37
| Inspect hydraulic oil relief valve, clean or replace as required | every 3000 hours |  | Ibid. page 38-39
| Inspect compressor base/crankcase, injection pump, head assembly | every 4000 hours |  | Ibid. page 40
| Inspect process inlet filter, replace as needed | every 4000 hours
| Inspect fuses, replace as needed | every 4000 hours
| Troubleshooting | as needed |  | Ibid. page 43
Edwards XDS35i Scroll Pump
| Inspect and clean inlet strainer | annual |  | Edwards XDS35i ScrollPump Manual page 25
| Inspect and clean gas ballast control | annual
| Clean the external fan cover | annual
| Replace tip seal and exhaust valve | annual | as required
| Test motor/drive condition | 15000 hours
| Replace bearings | 35000 hours
Polycold cryogenic chiller
| Verify expected function | daily | weekly | 214072.pdf page 189
| Check process temperatures | weekly
| Check process pressures | weekly
| Verify expected time to cool down | monthly
| Check for air flow from E-box fans | monthly
| Check system balance pressure | quarterly
| Verify LCD display not missing characters | quarterly
| Verify HMI keypad functions properly | quarterly
| Verify insulation intact | quarterly
| Verify oil level in compressor | quarterly
| Power cycle system (off for minimum of 10 seconds) | quarterly
| Replace fan filter (quarterly as needed else annual) | quarterly | annual
| Replace valve and valve components as necessary | annual
| Review event files for errors and backup system data | annual
| Check cool down cycle time, pressure, temperature | annual
| Check defrost cycle time, pressure, temperature | annual
| Verify water flow and temperature, check any water filters | annual
| Inspect frame, compressor, and components for wear | annual
| Reinsulate as appropriate | annual
| Perform compressor pump down test | annual
| Perform leak check on fittings and feedthroughs | annual
| Inspect all harness connections | annual
| Top off refrigerant charge | annual
| Evacuate and recharge as necessary | annual
| Clean electronic control box and replace motherboard as needed | annual | every 3-5 years
Leybold DV650 pumping system
| Check oil level | annual
| Oil change if using synthetic oil | annual
| Oil change if using PFPE | every 4 years
| Clean filter insert in cooling water pressure reducer | annual
| Check and clean gas ballast filter | annual
| Replace filter cartridge in purge gas pressure reducer | annual
| Check water hoses | annual | after long period without running
| Check purge gas hoses | annual
| Complete overhaul | as needed
| Leak check entire pump system | after maintenance/overhaul
| Check alarm and pump status in controller unit | as needed
| Troubleshooting | as needed |  | Ibid. page 81
Leybold WSU roots blowers (2001, 1001, 501)
| Oil change | after first 500 hours | every 3000 hours | Leybold ruvac ….pdf page 19
| Clean fan cowl and fins | as needed
| Clean inlet trap | as needed
| Clean pumping chamber (forced air or brush as necessary) | as needed
| Clean valve on pressure balance line and replace as necessary | as needed
| Troubleshooting | as needed |  | Ibid. page 23
Leybold Turbos (pumping cubes)
| Replace bearings | every 10000 hours |  | leybold turbos new style.pdf page 29
| Exchange rotor assembly | 45000 to 100000 hours
| Clean interior through bakeout | as needed | with increasing decline in base pressure
| Troubleshooting | as needed |  | Ibid. page 32
MKS gauges
| Verify zero reading and adjust as needed | after any power down
| Check for wear on cables and connectors | as needed
| Check inside gauge for dust/debris and clean as needed | after long standby at atm

## jensa_by_time
DAILY or ON START-UP
| JENSA compressor | Check lubricant oil level, top up as required
Check base frame lubricant pressure
Check cooling system flow, temperature, pressure
Check operation of control systems
Check inlet filter pressure drop
Verify inlet, interstage, and outlet pressures are normal
Check for abnormal noise or vibration
Check leak detection system gauges on both heads
| Polycold cryogenic chiller | Verify expected function
WEEKLY
| Polycold cryogenic chiller | Check process temperatures
Check process pressures
EVERY OTHER WEEK
| JENSA compressor | Disassemble and check inlet filter, replace/clean as required
MONTHLY
| Polycold cryogenic chiller | Verify expected time to cool down
Check for air flow from E-box fans
EVERY TWO MONTHS
| JENSA compressor | Change oil and oil filter elements, clean or replace strainer element
EVERY THREE MONTHS (QUARTERLY)
| Polycold cryogenic chiller | Check system balance pressure
Verify LCD display not missing characters
Verify HMI keypad functions properly
Verify insulation intact
Verify oil level in compressor
Power cycle system (off for minimum of 10 seconds)
Replace fan filter (quarterly as needed else annual)
EVERY FOUR MONTHS (TRIMESTERS)
| JENSA compressor | Inspect check valves, clean or replace as required
Inspect oil inlet check valves, clean or replace as required
Inspect hydraulic oil relief valve, clean or replace as required
| Leybold WSU roots blowers (2001, 1001, 501) | Oil change
EVERY SIX MONTHS
| JENSA compressor | Check operation of control systems
Check leak detection system gauges on both heads
Diaphragm and o-ring seal inspection/replacement
Inspect compressor base/crankcase, injection pump, head assembly
Inspect process inlet filter, replace as needed
Inspect fuses, replace as needed
ANNUALLY
| Edwards XDS35i Scroll Pump | Inspect and clean inlet strainer
Inspect and clean gas ballast control
Clean the external fan cover
Replace tip seal and exhaust valve
| Polycold cryogenic chiller | Replace valve and valve components as necessary
Review event files for errors and backup system data
Check cool down cycle time, pressure, temperature
Check defrost cycle time, pressure, temperature
Verify water flow and temperature, check any water filters
Inspect frame, compressor, and components for wear
Reinsulate as appropriate
Perform compressor pump down test
Perform leak check on fittings and feedthroughs
Inspect all harness connections
Top off refrigerant charge
Evacuate and recharge as necessary
Clean electronic control box and replace motherboard as needed
| Leybold DV650 pumping system | Check oil level
Oil change if using synthetic oil
Clean filter insert in cooling water pressure reducer
Check and clean gas ballast filter
Replace filter cartridge in purge gas pressure reducer
Check water hoses
Check purge gas hoses
| Leybold Turbos (pumping cubes) | Replace bearings
EVERY TWO YEARS
| Edwards XDS35i Scroll Pump | Test motor/drive condition
EVERY THREE TO FIVE YEARS
| Edwards XDS35i Scroll Pump | Replace bearings
| Polycold cryogenic chiller | Clean electronic control box and replace motherboard as needed
| Leybold DV650 pumping system | Oil change if using PFPE
| Leybold Turbos (pumping cubes) | Exchange rotor assembly
“AS NEEDED”, AFTER LONG SHUTDOWN, ETC
| JENSA compressor | Troubleshooting
| Edwards XDS35i Scroll Pump | Replace tip seal and exhaust valve
| Leybold DV650 pumping system | Check water hoses
Complete overhaul
Leak check entire pump system
Check alarm and pump status in controller unit
Troubleshooting
| Leybold Turbos (pumping cubes) | Clean interior through bakeout
Troubleshooting
| MKS gauges | Verify zero reading and adjust as needed
Check for wear on cables and connectors
Check inside gauge for dust/debris and clean as needed